## Slide 1: AIRFLOW REDUCTION IN CLEANROOMS
Manel Fernandez

## Slide 2: Disclaimer The views, opinions, and ideas expressed in this presentation are solely those of the presenter and do not necessarily reflect the official position, policies, or perspectives of Eli Lilly and Company. Any references to industry practices, research findings, or potential strategies are shared for informational purposes only and should not be interpreted as endorsements or directives from Lilly. Furthermore, while every effort has been made to ensure the accuracy and relevance of the information presented, it should not be considered as official guidance or regulatory advice. Attendees are encouraged to evaluate and adapt the content in accordance with their own professional judgment and applicable industry standards.

## Slide 3
2025
2015
2000
1950
Empirical approach. Focusing on maintaining air cleanliness rather than energy efficiency.
The pharmaceutical industry remained conservative, typically applying 20 to 50 ACR, depending on the cleanroom classification
ACR Optimization & Energy reduction programs
Demand-Controlled Filtration (DCF) and Fine-Tuning strategies to optimize ACR without compromising air quality.
> 80ACR
20 – 50 ACR
15 – 30 ACR

## Slide 4
ACR is not a regulatory requirement
Regulatory guidelines such as ISO 14644 and EU GMP Annex 1 do not mandate specific ACR values.
Oversized ACR leads to unnecessary energy consumption
High ACR values significantly increase HVAC energy demand, which accounts for 50-75% of total cleanroom energy consumption.
Airflow patterns are more important than ACR
Proper air distribution and contaminant removal efficiency (ventilation effectiveness) are more critical than simply increasing air changes per hour.
Particle generation rates should determine ACR
Cleanrooms are often over-ventilated due to uncertain particle generation rates.
A minimum ACR is still needed to maintain pressure differentials
While reducing airflow is beneficial, maintaining room pressurization (typically requiring at least 6 air changes per hour) is essential to prevent cross-contamination. Pressure stability must be considered when optimizing ACR.

## Slide 5
PARTICLE GENERATION - PROCESSES
Calculation of air supply rates and concentrations of airborne contamination in nonUDAF cleanrooms
European Journal of Parenteral & Pharmaceutical Sciences 2017; 22(4): 126-138
Particle Generation Characteristics
SMC Technical papers

## Slide 6
PARTICLE GENERATION - PEOPLE
Fundamentals of Air Cleaning Technology and Its Application in Cleanrooms
Zhonglin Xu – Ch.13 (2014)
Grades of activity

## Slide 7
Ventilation effectiveness in cleanrooms and its relation to decay rate, recovery rate, and air change rate
European Journal of Parenteral & Pharmaceutical Sciences 2018; 23(4):126–134
General particle concentration model and experimental validation for cleanrooms
Sådhanå (2020)45:198

## Slide 8
Air Change Rate Reduction during operation: Success at Roche/Genentech
Pharmaceutical Engineering – July / August 2023
YOUR TEXT HERE

## Slide 9
No operations are allowed, and no personnel access is permitted
Personnel
The airflow reduction mode is activated during night, weekends, or inactive periods
Activation
The rooms must be maintained within their GMP classification
Compliance
Differential pressure cascades must be always maintained, while temperature and relative humidity can have unoccupied setpoints.
Pressure, T & RH
Any ACR reduction strategy must be backed by validation studies to ensure compliance with particle count limits, microbial control, and recovery time requirements.
Validation
AIRFLOW REDUCTION APPROACH

## Slide 10
AIRFLOW REDUCTION MODE (BMS)
Schedule
A calendar must be available to define turn on/off the Airflow Reduction Mode
Access
Access to cleanroom shall be locked. Beacons in and out the cleanroom
Emergency changeover
Return to normal airflow shall be provided in case of emergency
Occupancy
Occupancy detectors to turn on ARM
Monitoring
Furthermore typical monitoring such as Temperature, Relative Humidity and Pressure, airflow shall monitored.
Building
Management
System

## Slide 11
MAL
PAL
FILLING
CW
LPHW
32 ºC
55 % RH
Dehum. 10 ºC
3194 m3/h
Airflow reduction
Cooling 18 ºC
Heating 18 ºC
30 Pa
30 Pa
45 Pa
28500 m3/h

## Slide 12
MAL
PAL
FILLING
CW
LPHW
32 ºC
55 % RH
Dehum. 12 ºC
2606 m3/h
Airflow reduction
Cooling 18 ºC
Heating 16 ºC
30 Pa
30 Pa
45 Pa
8600 m3/h
Setpoints
Airflow
Airflow
Airflow
Damper positioning
Damper positioning
Damper positioning
Presence detector
Beacon
Airflow

## Slide 13
ENERGY ANALYSIS – OUTDOOR CONDITIONS

## Slide 14
SIMULATION – OUTDOOR CONDITIONS

## Slide 15
SIMULATION – HEAT GAINS & HOURLY PROFILE

## Slide 16
SIMULATION – ENERGY ANALYSIS

## Slide 17
SIMULATION – ENERGY ANALYSIS
Chart: Sensible Cooling
Chart: Humidification
Chart: Recirculation Unit
Chart: Sensible Cooling
Chart: Heating
Chart: Heating
Chart: Humidification
 | MAX | ARM | NORMAL
Humidification | 25.0 Kg/h | 31952.5 Kg | 57265.6 Kg
 | MAX | ARM | NORMAL
Heating | 31.7 kW | 62821.6 kWh | 76331.5 kWh
 | MAX | ARM | NORMAL
Sensible Coooling | 16.6 kW | 6374.7 kWh | 6782.4 kWh
Chart: Latent Cooling
Chart: Latent Cooling
 | MAX | ARM | NORMAL
Cooling and Dehumidif. | 34.4 kW | 1745.3 kWh | 1887.2 kWh
 | MAX | ARM | NORMAL
Recirculation Unit | 43.6 kW | 212233.8 kWh | 309160.6 kWh
Chart: Recirculation Unit
6.0%
17.7%
31.4%
7.5%
44.2%

## Slide 18
SIMULATION – ENERGY ANALYSIS
Chart: Chiller Load (June – September)
Chart: Chiller Load (June – September)
 | MAX | ARM | NORMAL
Average Load - Year | 75 kW | 33.5 % | 48.4 %
30.8%

## Slide 19
SIMULATION – ENERGY ANALYSIS
MAKE UP UNIT – FULL MODE
MAKE UP UNIT - POWER
Airflows | Normal | kW | ARM | kW
Fresh Air | 3194 m³/h | 1.37 kW | 2606 m³/h | 1.12 kW
Supply Air | 28500 m³/h | 16.10 kW | 8600 m³/h | 7.77 kW
 | MAX | ARM | NORMAL
Fan | 17.5 kW | 115439.3 kWh | 153028.4 kWh
18.3%
RECIRCULATION UNIT - POWER
51.7%
43.4%
TOTAL VENTILATION ENERGY

## Slide 20
RECIRCULATING UNITS
Plenum Fan Filter Units
Compact Recirculating Units
In-Duct particle counters